## Outdoor DC UPS System Calculat
IO-Power Long-term Model Outdoor DC UPS Power System Calculation Formula (C-LiFePO4 Lithium Batteries)
Item | Device No.1 Power Consumption |  | Device No.2 Power Consumption |  | Device No.3 Power Consumption |  | Designed black-out hours Hours | Total consumption for impromptu black-out Watts | 6 Years Battery Aging Decay Rate Plus C-LiFePO4 Lithium Batteries used 6 Years Capacity Down to 90% Watts | Design of Battery Capacity Ah Definition@12.8V | Remark
| Day | Night | Day | Night | Day | Night
| 06:00-18:00 | 18:00-06:00 | 06:00-18:00 | 18:00-06:00 | 06:00-18:00 | 18:00-06:00
Please Fill in Your Data in blue area | 12 | 0 | 6 | 0 | 4 | 0 | 4 | 88 | 96.8 | 7.5625 | Do not need to change the battery in 6 years
Note 1: In response to your local build of street lighting system for low temperature difference, Please refer to the C-LiFePO4 Lithium Batteries discharge capacity of low temperature, increasing additional redundancy power capacity or project for battery heating protection (buried or strengthened coated insulation) 60% of the battery capacity@-10 ° C & 48%battery capacity 48%@-20 ° C
General Outdoor DC UPS Power System Calculation Formula (Deep Cycle Lead Acid Battery)
Item | Device No.1 Power Consumption |  | Device No.2 Power Consumption |  | Device No.3 Power Consumption |  | Designed black-out hours Hours | Total consumption for impromptu black-out Watts | 6 Years Battery Aging Decay Rate Plus Deep Cycle Lead Acid Battery used 1 year Capacity Down to 70% Watts | Design of Battery Capacity Ah Definition@12V | Remark
| Day | Night | Day | Night | Day | Night
| 06:00-18:00 | 18:00-06:00 | 06:00-18:00 | 18:00-06:00 | 06:00-18:00 | 18:00-06:00
Orange Area Will be Automatically Filled in | 12 | 0 | 6 | 0 | 4 | 0 | 4 | 88 | 132 | 11 | Batteries Should be Replaced 6 times at least in 6 Years
Note 1: The calculation formula of General lithium-ion batteries is similar as deep-cycle batteries. Both batteries can be calculated with this calculation formula
Note 2: special attention: deep cycle lead acid battery charge and discharge life is influenced by temperature. if the temperature lift every 8 degrees Celsius, the number of cycles reduces 50% (lead-acid batteries is generally defined @ 25 degrees Celsius for operating temperature)
General Outdoor DC UPS Power System Calculation Formula (General Lead Acid Battery)
Item | Device No.1 Power Consumption |  | Device No.2 Power Consumption |  | Device No.3 Power Consumption |  | Designed black-out hours Hours | Total consumption for impromptu black-out Watts | 6 Years Battery Aging Decay Rate Plus Lead Acid Battery used 1 year Capacity Down to 50% Watts | Design of Battery Capacity Ah Definition@12V | Remark
| Day | Night | Day | Night | Day | Night
| 06:00-18:00 | 18:00-06:00 | 06:00-18:00 | 18:00-06:00 | 06:00-18:00 | 18:00-06:00
Red Area Will be Automatically Filled in | 12 | 0 | 6 | 0 | 4 | 0 | 4 | 88 | 158.4 | 13.2 | Batteries Should be Replaced 12 times at least in 6 Years
Note 1: special attention: General lead acid battery charge and discharge life is influenced by temperature. if the temperature lift every 8 degrees Celsius, the number of cycles reduces 50% (lead-acid batteries is generally defined @ 25 degrees Celsius for operating temperature)