## Solar System Device1 Calculate
IO-Power Cloudy Weather Collection Model Solar Energy System Calculation Formula (C-LiFePO4 Lithium Batteries)
Item | Single Device Power Consumption |  | Day & Night Consumption Time Definition |  | Day & Night Power Consumption |  | 1 Day Total Power Consumption Watts | Expect Rainy Days | Device Operation |  | 3 Years Battery Aging Decay Rate Plus C-LiFePO4 Lithium Batteries used 3 Years Down to 90% Capacity Calculations | Operation Design |  | Design of Battery Capacity Ah 12.8V Definition | Solar Charging Hours Definition At the Lowest Sunshine Time Definition | Design of Solar Panel Total Wattage | Remark
| Day | Night | Day | Night | Day | Night |  |  | 2 | Days |  | 2 | Days
| 09:00-16:00 | 17:00-08:00 | 09:00-16:00 | 17:00-08:00 | Power consumption Watts |  |  |  | Total Power Consumption Watts |  |  | Total Power Consumption Watts
Blue Area Please Fill in Your Data | 15 | 15 | 0 | 17 | 0 | 255 | 255 | 2 | 510 |  | 110% | 561 |  | 43.8281 | 4 | 140.25 | 3 Years Do Not Need to Replace the Battery
Ps: IO-Power Cloudy Weather Collection Model Solar Energy System AM 09:00 ~ PM 04:00 Can Collect Small Solar Power Energy to Provide Device Operation Power and to Charge Battery
General Model Solar Energy System Calculation Formula (Deep Cycle Lead Acid Battery)
Item | Single Device Power Consumption |  | Day & Night Consumption Time Definition |  | Day & Night Power Consumption |  | 1 Day Total Power Consumption Watts | Expect Rainy Days | Device Operation |  | 3 Years Battery Aging Decay Rate Plus Deep Cycle Lead Acid Battery used 1 year Down to 70% Capacity Calculations | Operation Design |  | Design of Battery Capacity Ah 12V Definition | Solar Charging Hours Definition At the Lowest Sunshine Time Definition | Design of Solar Panel Total Wattage | Remark
| Day | Night | Day | Night | Day | Night |  |  | 2 | Days |  | 2 | Days
| 09:00-16:00 | 17:00-08:00 | 09:00-16:00 | 17:00-08:00 | Power consumption Watts |  |  |  | Total Power Consumption Watts |  |  | Total Power Consumption Watts
Orange Area Will be Automatically Filled in | 15 | 15 | 7 | 17 | 105 | 255 | 360 | 2 | 720 |  | 150% | 1080 |  | 90 | 4 | 270 | At Least 3 Years Should be Replaced 3 Batteries
Ps: General Li-Ion Solar DC UPS calculation is simmilar Deep Cycle Lead Acid Battery
General Model Solar Energy System Calculation Formula (General Lead Acid Battery)
Item | Single Device Power Consumption |  | Day & Night Consumption Time Definition |  | Day & Night Power Consumption |  | 1 Day Total Power Consumption Watts | Expect Rainy Days | Device Operation |  | 3 Years Battery Aging Decay Rate Plus General Lead Acid Battery used 0.5 year Down to 50% Capacity Calculations | Operation Design |  | Design of Battery Capacity Ah 12V Definition | Solar Charging Hours Definition At the Lowest Sunshine Time Definition | Design of Solar Panel Total Wattage | Remark
| Day | Night | Day | Night | Day | Night |  |  | 2 | Days |  | 2 | Days
| 09:00-16:00 | 17:00-08:00 | 09:00-16:00 | 17:00-08:00 | Power consumption Watts |  |  |  | Total Power Consumption Watts |  |  | Total Power Consumption Watts
Red Area Will be Automatically Filled in | 15 | 15 | 7 | 17 | 105 | 255 | 360 | 2 | 720 |  | 180% | 1296 |  | 108 | 4 | 324 | At Least 3 Years Should be Replaced 6 Batteries