## Street Lamps DC UPS System Calc
IO-Power Street Lamps Power Source Model DC UPS Power System Calculation Formula (C-LiFePO4 Lithium Batteries)
Item | Device No.1 Power Consumption |  | Device No.2 Power Consumption |  | Device No.3 Power Consumption |  | Designed Daytime Consumption Hours | Daytime total Power Consume Watts | 3 Years Battery Aging Decay Rate Plus C-LiFePO4 Lithium Batteries used 3 Years Capacity Down to 90% Watts | Designed Battery Capacity Ah Definition@ 12.8V | Nighttime power outage UPS Power function Number and timing Hours | Nighttime power outage UPS Power function Total Power Consumption Watts | 3 Years Battery Aging Decay Rate Plus C-LiFePO4 Lithium Batteries used 3 Years Capacity Down to 90% Watts | Design of Battery Capacity Ah Definition@12.8V | Remark
| Day | Night | Day | Night | Day | Night
| 06:00-18:00 | 18:00-06:00 | 06:00-18:00 | 18:00-06:00 | 06:00-18:00 | 18:00-06:00
Please Fill in Your Data in blue area | 12 | 0 | 6 | 0 | 4 | 0 | 14.3 | 314.6 | 346.06 | 27.0359 | 2 | 358.6 | 394.46 | 30.8172 | Do Not Need to Replace the Battery in 3 Years
Note 1: Designed daytime power consumption is the longest day time *115%, because in daytime, the light do not supply power from AM 06:00~PM 19:00, total of 13 hours, defined as 13*115%=14.9, which is recommended as designed power consumption during daytime
Note 2: The plus hour of nighttime power function is for the short balck-out in nighttime, avoiding power supply system at low power state and not fully charged, resulting in unable to supply enough electricity for equipment demands. So, we recommend suitable period of plus 2-3 hours
Note 3: In response to your local build of street lighting system for low temperature difference, Please refer to the C-LiFePO4 Lithium Batteries discharge capacity of low temperature, increasing additional redundancy power capacity or project for battery heating protection (buried or strengthened coated insulation) 60% of the battery capacity@-10 ° C & 48%battery capacity 48%@-20 ° C
General Street Lamps Power Source Model DC UPS Power System Calculation Formula (Deep Cycle Lead Acid Battery)
Item | Device No.1 Power Consumption |  | Device No.2 Power Consumption |  | Device No.3 Power Consumption |  | Designed Daytime Consumption Hours | Daytime total Power Consumption Watts | 3 Years Battery Aging Decay Rate Plus Deep Cycle Lead Acid Battery used 1 year Capacity Down to 70% Watts | Designed Battery Capacity Ah Definition@ 12V | Nighttime power outage UPS Power function Number and timing Hours | Nighttime power outage UPS Power function Total Power Consumption Watts | 3 Years Battery Aging Decay Rate Plus Deep Cycle Lead Acid Battery used 1 year Capacity Down to 70% Watts | Design of Battery Capacity Ah Definition@ 12V | Remark
| Day | Night | Day | Night | Day | Night
| 06:00-18:00 | 18:00-06:00 | 06:00-18:00 | 18:00-06:00 | 06:00-18:00 | 18:00-06:00
Orange Area Will be Automatically Filled in | 12 | 0 | 6 | 0 | 4 | 0 | 14.3 | 314.6 | 471.9 | 39.325 | 2 | 358.6 | 537.9 | 44.825 | Batteries Should be Replaced 3 times at least in 3 Years
Note 1: The calculation formula of General lithium-ion batteries is similar as deep-cycle batteries. Both batteries can be calculated with this calculation formula
Note 2: special attention: deep cycle lead acid battery charge and discharge life is influenced by temperature. if the temperature lift every 8 degrees Celsius, the number of cycles reduces 50% (lead-acid batteries is generally defined @ 25 degrees Celsius for operating temperature)
General Street Lamps Power Source Model DC UPS Power System Calculation Formula (General Lead Acid Battery)
Item | Device No.1 Power Consumption |  | Device No.2 Power Consumption |  | Device No.3 Power Consumption |  | Designed Daytime Consumption Hours | Daytime total Power Consumption Watts | 3 Years Battery Aging Decay Rate Plus General Lead Acid Battery used 1 year Capacity Down to 50% | Designed Battery Capacity Ah Definition @12V | Nighttime power outage UPS Power function Number and timing Hours | Night power outage UPS Power function Total Power Consumption Watts | 3 Years Battery Aging Decay Rate Plus General Lead Acid Battery used 1 year Down to 50% Capacity Calculations | Design of Battery Capacity Ah Definition@ 12V | Remark
| Day | Night | Day | Night | Day | Night
| 06:00-18:00 | 18:00-06:00 | 06:00-18:00 | 18:00-06:00 | 06:00-18:00 | 18:00-06:00
Red Area Will be Automatically Filled in | 12 | 0 | 6 | 0 | 4 | 0 | 14.3 | 314.6 | 566.28 | 47.19 | 2 | 358.6 | 645.48 | 53.79 | Batteries Should be Replaced 6 times at least in 3 Years
14.3